## Interconnection Request Form
| ITC | [16 empty] | Tracking Information
Received by:
| Interconnection Request Form (IRF) | [20 empty] | Date of receipt:
IRF Queue # :
IRF Rev # :
CNF Queue # :
CNF Rev # :
INSTRUCTIONS:
1. Request must be completed in its entirety (except for optional or non-applicable fields)
2. Queue date will be assigned when the completed, signed request is received at ITC.
3. When submitting revised IRF's, include the original IRF Queue # as well as the new rev number in the grey box.
The original document is rev 0 or no rev number, first revision is rev 1, etc. Changes should be in red text.
4. When submitting new or revised IRF's, include the Construction Notification Form (CNF) Queue # / Rev # in the grey box as applicable.
| 5. Complete Exhibit C if the distribution generator interconnection causes a 1 MW or greater increase in backflow onto the transmission | Complete Exhibit C for Distribution Generator interconnections >1MW or if the DG interconnection causes a 1 MW or greater increase in backflow onto the transmission for normal light load conditions (If DG or increase in backflow is <1MW, IRF is not needed.)
| 6. Complete Exhibit C if the distribution generator interconnection causes a 1 MW or greater increase in backflow onto the transmission | Complete Exhibit D for large loads where the aggregate expected peak load equals or exceeds 75 MW at a transmission level voltage at a site
| 7 | Please email the completed form to the address below and copy all relevant recipients.
|  | Email to: |  |  |  | customerinterconnections@itctransco.com
APPLICANT INFORMATION
Company Legal Name:
| Requester Name: | [21 empty] | Submittal Date:
Requester Title:
Requester Telephone Number:
E-mail Address (optional):
Mailing Address:
[8 empty] | City: | [8 empty] | State: |  |  |  | Zip Code:
INTERCONNECTION REQUEST TYPE*
Official Interconnection Request
Feasibility Request (Applicable to ITCT and METC only)
|  |  |  | System Impact Study | [6 empty] | Facility Feasibility Study
Anti-Islanding Request
INTERCONNECTION LOCATION INFORMATION
| Transmission Planner: | [7 empty] | ITCGP |  |  |  | ITCMW |  | ITCT | METC
County:
City/Township:
Address:
Specific Description (nearest cross streets, relationship to other identifiable facilities):
Balancing Authority/Local Balancing Authority (where load will be located or pseudo tied):
INTERCONNECTION INFORMATION
| Type of Request (check all that apply): | [12 empty] | Distribution Generator - Complete Exhibit C
|  |  | New Station |  |  |  |  | New Load |  |  |  | Add Transformer - # of xfrms |  |  |  |  | Replace Transformer | [5 empty] | Retirement/Decommission
|  |  | Other |  |  |  |  | Purchase Estimate Request | [6 empty] | Purchase Request |  |  |  | Confirm No Purchase
New or Existing Substation Name:
Proposed In-Service Date:
Nature of load (industrial, residential, etc.)
Required Information: (Include single-line diagram PDF attachment with this form)
Single-line diagram(s) including:
Existing and proposed facilities
Indication of ownership and demarcations
Location of metering
Load Addition/Change Form (Include separate forms for each delivery point affected)
Required Information as applicable:
Specification of any devices that may produce harmonic currents or voltage flicker (attach information)
Significant harmonic current (attach information)
Voltage fluctuation or imbalance (attach information)
TRANSFORMER SPECIFICATIONS
| Winding voltages: | [5 empty] | - | [8 empty] | Transformer MVA rating: |  |  |  | -
| Winding type (delta, wye): | [8 empty] | - | [5 empty] | Nameplate Impedance: |  |  |  | -
| # of Initial Transformer Connections requested: | [14 empty] | # of Future Transformer Connections requested:
PROJECT DESCRIPTION, NEED AND OTHER COMMENTS:
Revision Date: 05/21/2026
*Note: | Official Interconnection Requests indicate that the project is being budgeted for construction by the requestor and ITC will proceed with generating project creation necessary work to support the request.
Official Interconnection Requests signify that the end-use customer has either executed the required agreements (applicable only within ITCMW) or is actively negotiating such agreements with the requestor or Load Serving Entity (LSE).
Official Interconnection Requests will include system impact and facility feasibility studies as applicable/required.

## Load Change Form
Load Addition/Change Form
INSTRUCTIONS:
1. Complete Load/Addition Change Form for each substation load related to the project. MW load should be expressed in maximum amounts
2. Insert the Power Factor (PF) in cell "B19". If the PF is different for any specific load amount, override the cell formula by placing the expected MVAr load into the appropriate cell
3. Requestor may replace the year numbers with calendar years
Substation Name:
PSS/E Bus Number:
PSS/E Bus Name:
Check all that apply
New Load
Expanding Load
Reducing Load
Load Transfer
Transmission Line Tap (i.e., Pole Top Switch)
Projection of Real and Reactive Power Peak Requirements (MW and MVAR)
Load PF (pu) | Year 1 (In-Service Year) |  | Year 2 |  | Year 3 |  | Year 4 |  | Year 5 |  | Year 6 |  | Year 7 |  | Year 8 |  | Year 9 |  | Year 10
Enter PF Here | MW | MVAr | MW | MVAr | MW | MVAr | MW | MVAr | MW | MVAr | MW | MVAr | MW | MVAr | MW | MVAr | MW | MVAr | MW | MVAr
January |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
February |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
March |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
April |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
May |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
June |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
July |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
August |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
September |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
October |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
November |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
December |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
Yearly Maximum |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
Load Transfer Data (from bus)
|  | Year 1 |  | Year 2 |  | Year 3 |  | Year 4 |  | Year 5 |  | Year 6 |  | Year 7 |  | Year 8 |  | Year 9 |  | Year 10
PSS/E Bus Name* | PSS/E Bus # | MW | MVAr | MW | MVAr | MW | MVAr | MW | MVAr | MW | MVAr | MW | MVAr | MW | MVAr | MW | MVAr | MW | MVAr | MW | MVAr
*Note: Use full bus names (not PSSE abbreviated names)

## Exhibit C
EXHIBIT C
REQUEST FOR ITC EVALUATION OF DG INTERCONNECTION
IRF Number: |  | Revision:
Date Submitted:
Requester Contact Info:
Request Submitted by:
Submitter Phone #:
Requestor Email:
Company:
Distribution Generation Interconnection Information:
Substation Name (include one-line and map ):
Total Generation Proposed:
Substation Light Load (MW/MVAR):
Transformer (to which DG is connected) Light Load:
Backflow under light load (DG nameplate minus total sub load):
Fuel type of Resource:
MW Capacity of generation:
MVAR Capacity of generation:
Number and capacities of reactive equipment (Cap Banks, Reactors, SVC, etc):
Requested In Service Date:
Generator Step-Up or Substation Transformer Data:
MVA rating:
Voltage Rating:
% Impedance:
Fault Contribution (synchronous, transient, subtransient reactance, as applicable):
If Distribution substation has 1MW or greater aggregate DG connected to the substation prior to the DG interconnection request, please provide:
Aggregate MW Nameplate, by fuel type, at each distribution transformer:
Wind:
Solar:
Other
Other
Will a portable substation be required for the DG interconnection?
Is the DG output being sold elsewhere on the transmission system?
Other Considerations:
ITC EVALUATION RESPONSE
Response Date:
LIF Submittal Date:
Response Submitted By:
IRF # |  | Rev:
ITC Study Required? | Yes |  | No
Estimated Study Cost:
Estimated Study Duration :
Scope of Study Work:

## Exhibit D1
EXHIBIT D1
REQUEST FOR ADDITIONAL LARGE LOAD MODELING INFORMATION | Question | Response
No. | Question | Response
0 | Please provide the dynamic model or complete Exhibit D2. Dynamic models may be submitted in PSSE or TSAT format and should accurately represent fault ride-through performance, including all relevant control and protection functions. Exhibit D2 may be used to develop dynamic models; however, all dynamic models must be verified and validated by the interconnection customer. | Please enter file name here, if applicable.
1 | What is your data center’s total rated MW demand—including IT equipment, power distribution, and cooling? Please specify the current requested rated power and any planned increases over the next 10 years.
2 | What percentage of total MW consumption in the data center is due to computing/server, lighting, power distribution losses, and cooling?
3 | Identify the power factors associated with both the computing/server load and the cooling load, specifying whether each is leading or lagging.
3a | State whether the power factor remains constant or varies over time.
3b | Identify and describe any power factor correction devices, such as cap banks, and STATCOMS, such that they can be sufficiently modeled.
4 | How are the motor components of the cooling system driven? [Single-speed AC connected, VFD/inverter, other]
5 | Voltage sag levels where the load is disconnected from the utility and transferred to UPS or Backup Generation.
5a | What is the voltage sag level (% of nominal) and duration (seconds) at which server/digital load disconnects?
5b | What is the voltage sag level (% of nominal) and duration (seconds) at which cooling load disconnects?
6 | Voltage swell levels where the load is disconnected from the utility and transferred to UPS or backup generation.
6a | What is the voltage swell level (% of nominal) and duration (seconds) at which server/digital load disconnects?
6b | What is the voltage swell level (% of nominal) and duration (seconds) at which cooling load disconnects?
7 | Any frequency protection above/below which may disconnect? If so, please identify the protection settings.
8 | When the loads disconnect, and temporarily transfer to UPS, how are the loads reconnected to the utility grid? Please specify reconnection voltages, ramps and time delays.
8a | What is the delay in reconnecting once the voltage and frequency recovers to certain levels. Please specify the voltage and frequency levels and delays.
8b | If reconnection is performed as a stagger or ramp, please provide detailed information describing the timing and magnitude.
9 | Is the load expected to cycle up and down based on the anticipated application or machine learning computational process? If so, please specify load block cycling magnitude and frequency.
9a | If so, please describe the frequency (in Hz or period of cycle in seconds)(A&B&D in Figure 9) and magnitude (in MW or percentage of peak demand or X&Y % load) of expected variations.
9b | If possible, provide a .csv load profile showing variations in power during the training phase. | Please enter file name here, if applicable.
9c | Please provide information regarding the expected upward and downward load profile behavior (in MW/min) as seen in Figure 9 below (C1&C2).
Figure for 9:

## Exhibit D2
Dynamic Load Model Form
INSTRUCTIONS:
1. Complete Dynamic Load Model Form if a dynamic model file will not be provided at the time of request (numbers represented below are examples. Please provide planned site specific parameters).
2. Fields with clauclated values will have a note specifying so. There should not be a need to overwrite these values manually.
3. The Cooling Load, Static Load, and Non‑IT Load CMLD sections may include notes that provide example representative load types. If further comments are needed, please include feedback notes.
Load Info
Load Name | Load MW | Load MVAR
Insert Name | 100 | 100
Load Composition |  | Load Compositon (calculated values)
IT Loads (%) |  | IT Loads MW | 0
Cooling Loads (%) |  | IT Loads MVAR | #DIV/0!
Static (%) |  | Non-IT Loads MW | 0
IT Loads PF |  | Non-IT Loads MVAR | #DIV/0!
Non-IT Loads PF
IT Load Info
Load MW | Load MVAR
0 | #DIV/0!
Voltage Protection Settings
LVRT |  | HVRT
Low Voltage Set Point (pu) | Time Delay (s) | High Voltage Set Point (pu) | Time Delay (s)
0.9 | 2 | 1.1 | 0.5
0.8 | 0.5 | 1.2 | 0
0.5 | 0.15 | 1.2 | 0
0.5 | 0.15 | 1.2 | 0
Voltage Reconnection
Low Voltage Reconnection |  | High Voltage Reconnection
Voltage (pu) | 0.85 | Voltage (pu) | 1.1
Time Delay (s) | 1 | Time Delay (s) | 1
Ramp Rate (s) | 5 | Ramp Rate (s) | 5
Frequency Protection Settings
Low Frequency |  | High Frequency
Frequency (Hz) | 58 | Frequency (Hz) | 62
Time Delay (s) | 0.1 | Time Delay (s) | 0.1
Frequency Reconnection
Low Frequency Reconnection |  | High Frequency Reconnection
Frequency (Hz) | 58.5 | Frequency (Hz) | 61.5
Time Delay (s) | 0.2 | Time Delay (s) | 0.2
Ramp Rate (s) | 2 | Ramp Rate (s) | 2
Non IT Load Info (calculated values)
Total Load MW | 0
Total Load MVAR | #DIV/0!
Cooling Load MW | 0
Static Load MW | 0
Cooling Load Composition
Motor A | 100%
Motor B | 0%
Motor C | 0%
Motor D | 0%
Electronic | 0%
Static Load Composition
Contant Current Load | 100%
Constant Resistance Load | 0%
Non IT Load CMLD Composition (calculated values)
Motor A | #DIV/0!
Motor B | #DIV/0!
Motor C | #DIV/0!
Motor D | #DIV/0!
Electronic | #DIV/0!
Note on D13: Calculated from first block information - do not manually enter
Note on D14: Calculated from first block information - do not manually enter
Note on D15: Calculated from first block information - do not manually enter
Note on D16: Calculated from first block information - do not manually enter
Note on B22: Calculated from first block information - do not manually enter
Note on C22: Calculated from first block information - do not manually enter
Note on B51: Calculated from first block information - do not manually enter
Note on B52: Calculated from first block information - do not manually enter
Note on B53: Calculated from first block information - do not manually enter
Note on B54: Calculated from first block information - do not manually enter
Note on B57: Commercial compressor-heavy AC bucket, often up to ~250 hp in utility practice
Note on B58: Large HVAC plant motors (big fans / big pumps / large centrifugal compressor drives)
Note on B59: Smaller variable-torque HVAC auxiliaries (small fans / small pumps)
Note on B60: single-phase residential AC / heat-pump cooling bucket
Note on B61: VFD-driven pumps / fans / compressors
Note on B64: J+30 e.g. lighting
Note on B65: J+28 e.g. heating & cooking
Note on B69: J+18
Note on B70: J+19
Note on B71: J+20
Note on B72: J+21
Note on B73: J+22

## Revision History
Revision History
Date | Revision | Description
2026-01-16 | 0 | Initial Creation
2026-03-31 | 1 | Added Exhibit D1 & D2, Renamed sheet to Interconnection Request Form and added instruction #6.
2026-05-21 | 2 | Modified the Load Change Form and provided additional clarity in the instructions to populate maximum load amounts